## Calcs
[9 empty] | Supply fan power allowances = 1, Otherwise = 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0
[10 empty] | Return or exhaust systems required by code or accreditation standards to be fully ducted, or systems required to maintain air pressure differentials between adjacent rooms | Return or exhaust systems required by code or accreditation standards to be fully ducted, or systems required to maintain air pressure differentials between adjacent rooms | Exhaust filters, scrubbers, or other exhaust treatment required by code or standard. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | Filtration Allowance for > Merv 16 or HEPA Filter (two times the clean filter pressure dropmid-life) 2 | Allowance for gas phase filtration required by code or accredited standard. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | Biosafety cabinet. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | Exhaust System Base Allowance | Energy Recovery Allowance for 0.60 ≤ ERR <0.65 | Energy Recovery Allowance for 0.60 ≤ ERR <0.65 | Filter (any MERV value)2 | Low-turndown single-zone VAV fan systems meeting the requirements in note 7. | Coil Runaround Loop | Coil Runaround Loop
[8 empty] | SysType | FlowCap | Exhaust systems required by code to be fully ducted | Return systems required by code to be fully ducted | Exhaust filters, scrubbers, or other exhaust treatment (calculation required, see note) | Particulate filtration credit: MERV 16 or greater and electronically enhanced filters | Carbon and other gas-phase air cleaners (calculation required, see note) | Biosafety cabinet (calculation required, see note) | Exhaust Systems Base Allowance | Supply - Energy Recovery (Enthalpy Recovery Ratio ? 0.60 and <0.65) | Return - Energy Recovery (Enthalpy Recovery Ratio ? 0.60 and <0.65) | Return - Filter (any MERV value) | Single Zone VAV Systems that are capable of turning down to 50% of full load airflow at a maximum of 30% design wattage | Supply -Coil Runaround Loop | Return - Coil Runaround Loop
[8 empty] | MultiZoneVAV | ≤5,000 cfm | 0.116 | 0.116 | 0.231 | 0.335 | 0.224 | 0.231 | 0.221 | 0.184 | 0.19 | 0.046 | 0 | 0.135 | 0.139
[8 empty] | MultiZoneVAV | >5,000 and ≤10,000 cfm | 0.1 | 0.1 | 0.198 | 0.28 | 0.188 | 0.198 | 0.246 | 0.155 | 0.163 | 0.041 | 0 | 0.114 | 0.12
[8 empty] | MultiZoneVAV | >10,000 cfm | 0.089 | 0.089 | 0.177 | 0.265 | 0.176 | 0.177 | 0.236 | 0.144 | 0.146 | 0.036 | 0 | 0.105 | 0.107
[8 empty] | AllOther | ≤5,000 cfm | 0.116 | 0.116 | 0.232 | 0.342 | 0.231 | 0.232 | 0.186 | 0.19 | 0.191 | 0.046 | 0.07 | 0.139 | 0.139
[8 empty] | AllOther | >5,000 and ≤10,000 cfm | 0.102 | 0.102 | 0.202 | 0.292 | 0.197 | 0.202 | 0.184 | 0.163 | 0.166 | 0.041 | 0.1 | 0.12 | 0.123
[8 empty] | AllOther | >10,000 cfm | 0.091 | 0.091 | 0.179 | 0.264 | 0.177 | 0.179 | 0.19 | 0.146 | 0.148 | 0.035 | 0.089 | 0.107 | 0.109
[21 empty] | As SZSys | As MZSys
[9 empty] | Calculated Values | 3a - SZAC | 3b - SZHP (no furnace) | 3c - SZHP (with furnace) | 7a - SZVAVAC | 7b - SZVAVHP (no furnace) | 7c - SZVAVHP (with furnace) | 5 - PVAV | 6 - VAV | 9 - HEATVENT | 13a - BKICHMAU | 13b - PKITCHMAU | 14 - 4PSZVAV | 14 - 4PSZVAV | 15 - PVAVAWHP |  | From CEC in an email, dated 7/5/2023
[9 empty] | ≤5,000 cfm | 0.8 | 0.742 | 0.8 | 0.8 | 0.742 | 0.8 | 0.978 | 0.978 | 0.615 | 0.602 | 0.614 | 0.626 | 0.712 | 0.978
[9 empty] | >5,000 and ≤10,000 cfm | 0.78 | 0.72 | 0.78 | 0.78 | 0.72 | 0.78 | 1.013 | 1.013 | 0.62 | 0.586 | 0.596 | 0.646 | 0.729 | 1.013
TABLE 140.4-A: Supply Fan Power Allowances (watts/cfm) | [8 empty] | >10,000 cfm | 0.748 | 0.676 | 0.748 | 0.748 | 0.676 | 0.748 | 0.946 | 0.946 | 0.605 | 0.54 | 0.558 | 0.611 | 0.675 | 0.946
x |  | Multi-Zone VAV Systems ≤5,000 cfm | Multi-Zone VAV Systems >5,000 and ≤10,000 cfm | Multi-Zone VAV Systems >10,000 cfm | All Other Fan Systems ≤5,000 cfm | All Other Fan Systems >5,000 and ≤10,000 cfm | All Other Fan Systems >10,000 cfm |  | Is Multi-Zone System? | [6 empty] | x | x |  |  |  |  | x | x | 4
x | Supply System Base Allowance for AHU Serving Spaces < 6 Floors Away. | 0.395 | 0.453 | 0.413 | 0.232 | 0.256 | 0.236 |  | Supply System Base Allowance for AHU Serving Spaces < 6 Floors Away. | x | x | x | x | x | x | x | x | x | x | x | x | x | x | 14
x | Supply System Base Allowance for AHU Serving Spaces > 6 Floors Away | 0.508 | 0.548 | 0.501 | 0.349 | 0.356 | 0.325 |  | Supply System Base Allowance for AHU Serving Spaces > 6 Floors Away | [14 empty] | 0
x | MERV 13 to MERV 16 Filter Upstream of Thermal Conditioning Equipment (two times the clean filter pressure dropmid-life)2 | 0.136 | 0.114 | 0.105 | 0.139 | 0.12 | 0.107 |  | MERV 13 to MERV 16 Filter Upstream of Thermal Conditioning Equipment (two times the clean filter pressure dropmid-life)2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | 14
x | MERV 13 to MERV 16 Final Filter Downstream of Thermal Conditioning Equipment. (two times the clean filter pressure dropmid-life) 2 | 0.225 | 0.188 | 0.176 | 0.231 | 0.197 | 0.177 |  | MERV 13 to MERV 16 Final Filter Downstream of Thermal Conditioning Equipment. (two times the clean filter pressure dropmid-life) 2 | [14 empty] | 0
x | Filtration Allowance for > Merv 16 or HEPA Filter (two times the clean filter pressure dropmid-life) 2 | 0.335 | 0.28 | 0.265 | 0.342 | 0.292 | 0.264 |  | Filtration Allowance for > Merv 16 or HEPA Filter (two times the clean filter pressure dropmid-life) 2 | [14 empty] | 0
x | Central Hydronic Heating Coil Allowance | 0.046 | 0.048 | 0.052 | 0.046 | 0.05 | 0.054 |  | Central Hydronic Heating Coil Allowance | [6 empty] | x | x |  | x |  | x | x | x | 6
x | Electric Heat Allowance | 0.046 | 0.038 | 0.035 | 0.046 | 0.04 | 0.036 |  | Electric Heat Allowance | [14 empty] | 1
x | Gas Heat Allowance | 0.069 | 0.057 | 0.07 | 0.058 | 0.06 | 0.072 |  | Gas Heat Allowance | x |  | x | x |  | x |  |  | x |  | x |  |  |  | 6
x | Hydronic/DX Cooling Coil, or Heat Pump Coil (wet) Allowance | 0.135 | 0.114 | 0.105 | 0.139 | 0.12 | 0.107 |  | Hydronic/DX Cooling Coil, or Heat Pump Coil (wet) Allowance | x | x | x | x | x | x | x | x |  | x | x | x | x | x | 13
x | Solid or Liquid Desiccant System Allowance | 0.157 | 0.132 | 0.123 | 0.163 | 0.139 | 0.124 |  | Solid or Liquid Desiccant System Allowance | [14 empty] | 0
x | Reheat Coil for Dehumidification Allowance | 0.045 | 0.038 | 0.035 | 0.046 | 0.04 | 0.036 |  | Reheat Coil for Dehumidification Allowance | [14 empty] | 0
x | Allowance for evaporative humidifier/cooler in series with a cooling coil. Value shown is allowed watts/cfm per 1.0 in. wg. Determine pressure loss (in. wg) at 400 fpm or maximum velocity allowed by the manufacturer, whichever is less. [Calculation required, see note 4] | 0.224 | 0.188 | 0.176 | 0.231 | 0.197 | 0.177 |  | Allowance for evaporative humidifier/cooler in series with a cooling coil. Value shown is allowed watts/cfm per 1.0 in. wg. Determine pressure loss (in. wg) at 400 fpm or maximum velocity allowed by the manufacturer, whichever is less. [Calculation required, see note 4] | [14 empty] | 0
x | Allowance for 100% outdoor air system meeting the requirements of Note 5. | 0 | 0 | 0 | 0.07 | 0.1 | 0.107 |  | Allowance for 100% outdoor air system meeting the requirements of Note 5. | [11 empty] | x | x |  | 2
x | Energy Recovery Allowance for 0.50 ≤ ERR <0.55 | 0.135 | 0.114 | 0.105 | 0.139 | 0.12 | 0.107 |  | Energy Recovery Allowance for 0.50 ≤ ERR <0.55 | [14 empty] | 0
x | Energy Recovery Allowance for 0.55 ≤ ERR <0.60 | 0.16 | 0.134 | 0.124 | 0.165 | 0.141 | 0.126 |  | Energy Recovery Allowance for 0.55 ≤ ERR <0.60 | [14 empty] | 0
x | Energy Recovery Allowance for 0.60 ≤ ERR <0.65 | 0.184 | 0.155 | 0.144 | 0.19 | 0.163 | 0.146 |  | Energy Recovery Allowance for 0.60 ≤ ERR <0.65 | [14 empty] | 1
x | Energy Recovery Allowance for 0.65 ≤ ERR <0.70 | 0.208 | 0.175 | 0.163 | 0.215 | 0.184 | 0.165 |  | Energy Recovery Allowance for 0.65 ≤ ERR <0.70 | [14 empty] | 0
x | Energy Recovery Allowance for 0.70 ≤ ERR <0.75 | 0.232 | 0.196 | 0.183 | 0.24 | 0.205 | 0.184 |  | Energy Recovery Allowance for 0.70 ≤ ERR <0.75 | [14 empty] | 0
x | Energy Recovery Allowance for 0.75 ≤ ERR <0.80 | 0.257 | 0.216 | 0.202 | 0.264 | 0.226 | 0.203 |  | Energy Recovery Allowance for 0.75 ≤ ERR <0.80 | [14 empty] | 0
x | Energy Recovery Allowance for ERR ≥ 0.80 | 0.281 | 0.236 | 0.222 | 0.289 | 0.247 | 0.222 |  | Energy Recovery Allowance for ERR ≥ 0.80 | [14 empty] | 0
x | Coil Runaround Loop | 0.135 | 0.114 | 0.105 | 0.139 | 0.12 | 0.107 |  | Coil Runaround Loop | [14 empty] | 1
x | Allowance for gas phase filtration required by code or accredited standard. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | 0.224 | 0.188 | 0.176 | 0.231 | 0.197 | 0.177 |  | Allowance for gas phase filtration required by code or accredited standard. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | [14 empty] | 0
x | Economizer Return Damper | 0.045 | 0.038 | 0.035 | 0.046 | 0.04 | 0.036 |  | Economizer Return Damper | x | x | x | x | x | x | x | x |  | x | x |  |  | x | 11
x | Air Blender Allowance | 0.045 | 0.038 | 0.035 | 0.046 | 0.04 | 0.036 |  | Air Blender Allowance | [14 empty] | 0
x | Allowance for sound attenuation section [fans serving spaces with design background noise goals below NC35]. | 0.034 | 0.029 | 0.026 | 0.035 | 0.03 | 0.027 |  | Allowance for sound attenuation section [fans serving spaces with design background noise goals below NC35]. | [14 empty] | 0
x | Deduction for systems that feed a terminal unit with a fan with electrical input power < 1kW. | -0.1 | -0.1 | -0.1 | -0.1 | -0.1 | -0.1 |  | Deduction for systems that feed a terminal unit with a fan with electrical input power < 1kW. | [14 empty] | 0
x | Low-turndown single-zone VAV fan systems meeting the requirements in note 7. | 0 | 0 | 0 | 0.07 | 0.1 | 0.089 |  | Low-turndown single-zone VAV fan systems meeting the requirements in note 7. | [14 empty] | 0
x | 1. See FAN SYSTEM, MULTI-ZONE VARIABLE AIR VOLUME (VAV) in definition a Multi-Zone VAV System. | [7 empty] | x | [14 empty] | 0
x | 2. Filter fan power allowance can only be counted once per fan system. | [7 empty] | x | [14 empty] | 0
x | 3. RESERVED. | [7 empty] | x | [14 empty] | 0
x | 4. Power allowance requires further calculation by multiplying the actual in. wg. of the device/ component by the watts/ cfm in Table 170.2-B. | [7 empty] | x | [14 empty] | 0
x | 5. The 100% outdoor air system must serve 3 or more HVAC zones and airflow during non-economizer operating periods must not exceed 135% of minimum requirements in Section 120.1(c)(3). | [7 empty] | x | [14 empty] | 0
x | 6. Energy Recovery Ratio (ERR) calculated per ANSI/ASHRAE 84-2020. | [7 empty] | x | [14 empty] | 0
x | 7. A low-turndown single-zone VAV fan system must be capable of and configured to reduce airflow to 50 percent of design airflow and use no more than | [7 empty] | x | [14 empty] | 0
x | 30 percent of the design wattage at that airflow. No more than 10 percent of the design load served by the equipment shall have fixed loads. | [7 empty] | x | [14 empty] | 0
x | [8 empty] | x | [14 empty] | 0
x | [8 empty] | x | [14 empty] | 0
TABLE 140.4-B: EXHAUST, RETURN, RELIEF, TRANSFER FAN POWER ALLOWANCES (CFM/WATT) | [8 empty] | x | [14 empty] | 0
x |  | Multi-Zone VAV Systems ≤5,000 cfm1 | Multi-Zone VAV Systems >5,000 and ≤10,000 cfm1 | Multi-Zone VAV Systems >10,000 cfm1 | All Other Fan Systems ≤5,000 cfm | All Other Fan Systems >5,000 and ≤10,000 cfm | All Other Fan Systems >10,000 cfm |  | x | [14 empty] | 0
x | Exhaust System Base Allowance | 0.221 | 0.246 | 0.236 | 0.186 | 0.184 | 0.19 |  | Exhaust System Base Allowance | x | x | x | x | x | x | x | x | x |  |  |  |  | x | 10
x | Filter (any MERV value)2 | 0.046 | 0.041 | 0.036 | 0.046 | 0.041 | 0.035 |  | Filter (any MERV value)2 | [14 empty] | 0
x | Energy Recovery Allowance for 0.50 ≤ ERR <0.55 | 0.139 | 0.12 | 0.107 | 0.139 | 0.123 | 0.109 |  | Energy Recovery Allowance for 0.50 ≤ ERR <0.55 | [14 empty] | 0
x | Energy Recovery Allowance for 0.55 ≤ ERR <0.60 | 0.165 | 0.142 | 0.126 | 0.165 | 0.144 | 0.128 |  | Energy Recovery Allowance for 0.55 ≤ ERR <0.60 | [14 empty] | 0
x | Energy Recovery Allowance for 0.60 ≤ ERR <0.65 | 0.19 | 0.163 | 0.146 | 0.191 | 0.166 | 0.148 |  | Energy Recovery Allowance for 0.60 ≤ ERR <0.65 | [14 empty] | 1
x | Energy Recovery Allowance for 0.65 ≤ ERR <0.70 | 0.215 | 0.184 | 0.165 | 0.216 | 0.188 | 0.167 |  | Energy Recovery Allowance for 0.65 ≤ ERR <0.70 | [14 empty] | 0
x | Energy Recovery Allowance for 0.70 ≤ ERR <0.75 | 0.24 | 0.206 | 0.184 | 0.241 | 0.209 | 0.186 |  | Energy Recovery Allowance for 0.70 ≤ ERR <0.75 | [14 empty] | 0
x | Energy Recovery Allowance for 0.75 ≤ ERR <0.80 | 0.265 | 0.227 | 0.203 | 0.266 | 0.231 | 0.205 |  | Energy Recovery Allowance for 0.75 ≤ ERR <0.80 | [14 empty] | 0
x | Energy Recovery Allowance for ERR ≥ 0.80 | 0.289 | 0.248 | 0.222 | 0.291 | 0.252 | 0.225 |  | Energy Recovery Allowance for ERR ≥ 0.80 | [14 empty] | 0
x | Coil Runaround Loop | 0.139 | 0.12 | 0.107 | 0.139 | 0.123 | 0.109 |  | Coil Runaround Loop | [14 empty] | 1
x | Economizer return damper |  |  | 0.036 |  |  | 0.037 |  | Economizer return damper | [14 empty] | 0
x | Return or exhaust systems required by code or accreditation standards to be fully ducted, or systems required to maintain air pressure differentials between adjacent rooms | 0.116 | 0.1 | 0.089 | 0.116 | 0.102 | 0.091 |  | Return or exhaust systems required by code or accreditation standards to be fully ducted, or systems required to maintain air pressure differentials between adjacent rooms | [14 empty] | 0
x | Return and/or exhaust airflow control devices required for space pressurization control | 0.116 | 0.1 | 0.089 | 0.116 | 0.102 | 0.091 |  | Return and/or exhaust airflow control devices required for space pressurization control | [14 empty] | 0
x | Laboratory and vivarium exhaust systems in high- rise buildings for vertical duct exceeding 75 ft. Value shown is allowed w/cfm per 0.25 in. wg for each 100 feet exceeding 75 feet. [Calculation required, see note 4] | 0.058 | 0.051 | 0.045 | 0.058 | 0.052 | 0.046 |  | Laboratory and vivarium exhaust systems in high- rise buildings for vertical duct exceeding 75 ft. Value shown is allowed w/cfm per 0.25 in. wg for each 100 feet exceeding 75 feet. [Calculation required, see note 4] | [14 empty] | 0
x | Biosafety cabinet. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | 0.231 | 0.198 | 0.177 | 0.232 | 0.202 | 0.179 |  | Biosafety cabinet. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | [14 empty] | 0
x | Exhaust filters, scrubbers, or other exhaust treatment required by code or standard. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | 0.231 | 0.198 | 0.177 | 0.232 | 0.202 | 0.179 |  | Exhaust filters, scrubbers, or other exhaust treatment required by code or standard. Value shown is allowed w/cfm per 1.0 in. wg air pressure drop. [Calculation required, see note 4] | [14 empty] | 0
x | Sound attenuation section [Fans serving spaces with design background noise goals below NC35.] | 0.035 | 0.03 | 0.027 | 0.035 | 0.031 | 0.028 |  | Sound attenuation section [Fans serving spaces with design background noise goals below NC35.] | [14 empty] | 0
x | 1. For requirements to be classified as a Multi-Zone VAV System see definition for Multi-Zone Variable Air Volume Fan System.
x | 2. Filter pressure loss can only be counted once per fan system.
x | 3.Energy Recovery Ratio (ERR) calculated per ANSI/ASHRAE 84-2020.
x | 4. Power allowance requires further calculation, multiplying the actual pressure drop (in. wg.) of the device/ component by the watts/cfm in the Table 170.2-C.
Note on V28: Jireh Peng: Only one coil with changeover valve

## For CSV
;
TABLE T24N_2025FanPwrIdxAdj
; |  |  | Exhaust systems required by code to be fully ducted | Return systems required by code to be fully ducted | Exhaust filters, scrubbers, or other exhaust treatment (calculation required, see note) | Particulate filtration credit: MERV 16 or greater and electronically enhanced filters | Carbon and other gas-phase air cleaners (calculation required, see note) | Biosafety cabinet (calculation required, see note) | Exhaust Systems Base Allowance | Supply - Energy Recovery (Enthalpy Recovery Ratio ? 0.60 and <0.65) | Return - Energy Recovery (Enthalpy Recovery Ratio ? 0.60 and <0.65) | Return - Filter (any MERV value) | Single Zone VAV Systems that are capable of turning down to 50% of full load airflow at a maximum of 30% design wattage | Supply -Coil Runaround Loop | Return - Coil Runaround Loop
| SysType | FlowCap | FullyDuctedExh | FullyDuctedRet | ExhFilters | MERVGTE16 | GasPhaseAirCleaners | BiosftyCabExh | ExhBaseAllow | ERVSupply | ERVReturn | RetFilter | SZVAV | ERVCoilRunaroundSupply | ERVCoilRunaroundReturn
| MultiZoneVAV | <=5000 | 0.116 | 0.116 | 0.231 | 0.335 | 0.224 | 0.231 | 0.221 | 0.184 | 0.19 | 0.046 | 0 | 0.135 | 0.139
| MultiZoneVAV | <=10000 | 0.1 | 0.1 | 0.198 | 0.28 | 0.188 | 0.198 | 0.246 | 0.155 | 0.163 | 0.041 | 0 | 0.114 | 0.12
| MultiZoneVAV | >10000 | 0.089 | 0.089 | 0.177 | 0.265 | 0.176 | 0.177 | 0.236 | 0.144 | 0.146 | 0.036 | 0 | 0.105 | 0.107
| AllOther | <=5000 | 0.116 | 0.116 | 0.232 | 0.342 | 0.231 | 0.232 | 0.186 | 0.19 | 0.191 | 0.046 | 0.07 | 0.139 | 0.139
| AllOther | <=10000 | 0.102 | 0.102 | 0.202 | 0.292 | 0.197 | 0.202 | 0.184 | 0.163 | 0.166 | 0.041 | 0.1 | 0.12 | 0.123
| AllOther | >10000 | 0.091 | 0.091 | 0.179 | 0.264 | 0.177 | 0.179 | 0.19 | 0.146 | 0.148 | 0.035 | 0.089 | 0.107 | 0.109
ENDTABLE
;
TABLE T24N_2025BaseFanPwrIdx
; |  |  | 3a – SZAC | 3b – SZHP (no furnace) | 3c – SZDFHP (with furnace) | 7a – SZVAVAC | 7b – SZVAVHP | 7c – SZVAVDFHP (with furnace) | 5 – PVAV | 6 – VAV | 9 – HEATVENT | 13a - BKICHMAU | 13b - PKITCHMAU | 14 - 4PSZVAV | 14 - 4PSZVAV | 15 - PVAVAWHP
|  | FlowCap | Sys3a | Sys3b | Sys3c | Sys7a | Sys7b | Sys7c | Sys5 | Sys6 | Sys9 | Sys13a | Sys13b | Sys14s | Sys14m | Sys15
|  | <=5000 | 0.8 | 0.742 | 0.8 | 0.8 | 0.742 | 0.8 | 0.978 | 0.978 | 0.615 | 0.602 | 0.614 | 0.626 | 0.712 | 0.978
|  | <=10000 | 0.78 | 0.72 | 0.78 | 0.78 | 0.72 | 0.78 | 1.013 | 1.013 | 0.62 | 0.586 | 0.596 | 0.646 | 0.729 | 1.013
|  | >10000 | 0.748 | 0.676 | 0.748 | 0.748 | 0.676 | 0.748 | 0.946 | 0.946 | 0.605 | 0.54 | 0.558 | 0.611 | 0.675 | 0.946
ENDTABLE
;
TABLE T24N_2025AddBaseFanPwrIdxForEAA
; |  |  | MZ-VAV (Systems 5, 6, 14, and 15) | All other (Systems 1, 3, 7, and 9)
|  | FlowCap | MZVAV | AllOther
|  | <=5000 | 0.205 | 0.209
|  | <=10000 | 0.174 | 0.182
|  | >10000 | 0.159 | 0.162
ENDTABLE